**COVID-19 VISITATION BOOTHS**

 **LIFE SAFETY CODE REQUIREMENTS**

**For visitation booths to be temporary constructed and used during the COVID-19 pandemic, the following would be the minimum requirements:**

**Means of Egress**

All required means of egress routes must be constantly maintained throughout from any point of origin, to include the exit discharge to the public way. [NFPA 101 19.2, NFPA 101 33.2, NFPA 101 33.3.2, NFPA 101 7.5.1.1, & NFPA 101 7.1.10.1]

**Materials**

1. If built and used **inside** the facility the materials would be required to meet a minimum Class B finish rating. Class B finish is characterized by the following:
	1. Flame spread index, 26-75
	2. Smoke developed index, 0-450

[NFPA 101 19.3.3, 10.2.1.4]

1. If light-transmitting plastic panels (acrylic, acrylic glass, plexiglass, etc.) are used they are required to be a minimum 0.080” thickness [IBC 2401, ANSI Z97.1]

**Construction of Visitation Booths**

1. Visitation booths to be constructed and used shall ensure anti-tipping measures are in place.

[Rules & Regulations 1200-08-06-.08(1), Rules & Regulations 1200-08-11-.07(1), Rules & Regulations 1200-08-25-.09(1)]